## Slide 1
AQUAPHY
Independent safety interlock
for water-treatment dosing
CyberMACS Summer School 2026 Hackathon
Team PUREIT (Track A · Resilience Under Attack)
Amaan Rais Shah · Amar Kumar Mandal · Mahdi Mohammad Shibli · Quazi Fariha Tasnim · S M Dedar Alam

## Slide 2
The threat to water treatment
CyberMACS Summer School 2026 Hackathon
02
Valid credentials can carry
an unsafe dosing command.
Compromised operator access
SCADA accepts the command.
The PLC executes the setpoint.
Safety and availability
Reject unsafe dosing while
maintaining water service.
Defender: CyberCity's SCADA operator. Grounded in the 2021 Oldsmar attack.
Notes: A compromised operator credential permits malicious commands through legitimate SCADA channels. Network authentication alone does not establish that a dosing command is physically safe. The intended defender is the operator on shift. A full shutdown can threaten water pressure, firefighting capacity and backflow protection.

## Slide 3
An independent safety layer
CyberMACS Summer School 2026 Hackathon
03
01
SCADA command
02
SIS interlock
03
Dosing pump
Requested dose
Three safety gates
Independent verification
Only permitted
commands pass
SIS = Safety Instrumented System
Notes: The prototype models a Safety Instrumented System (SIS) between SCADA and the dosing pump. Independence is an architectural objective. Real hardware isolation and a physical key switch remain future work. The source describes inspiration from IEC 61511 / ISA-84, not achieved certification.

## Slide 4
Three safety gates
CyberMACS Summer School 2026 Hackathon
04
150 ppm
Concentration ceiling
Projected finished-water
concentration
40 ppm/s
Slew-rate limit
Maximum rate of
dose change
15%
Sensor tolerance
Independent channels
checked over multiple samples
Prototype settings. Plant-specific safety validation remains required.
Notes: Gate 1 limits projected resulting finished-water concentration, rather than raw pump stroke, to address both direct dosing and flow-spoofing scenarios. Gate 2 rejects dose changes faster than 40 ppm per second. Gate 3 cross-checks independent sensor channels within 15% across multiple samples. These are team-selected prototype thresholds, not validated drinking-water limits or universal industrial settings.

## Slide 5
Response to a sustained attack
CyberMACS Summer School 2026 Hackathon
05
5
consecutive
blocked commands
Gradual dosing reduction
Return toward the configured
100 ppm baseline.
Maintain plant operation during the response.
Notes: After five consecutive blocked commands, the prototype invokes its fail-safe decay policy. Dosing steps down smoothly toward the configured 100 ppm baseline while the plant continues operating. This is the prototype policy, not a claim of certified process safety.

## Slide 6
Live demonstration
CyberMACS Summer School 2026 Hackathon
06
Requested dose
The attacker’s “Ghost Line”
Applied dose
The command that passes
the safety checks
FastAPI dashboard with real-time charts
Audit log
Attack flow and response
Notes: The team describes a FastAPI control-room dashboard with real-time charts. The Ghost Line shows the attacker-requested dose beside the dose that reaches the simulated water process. Every blocked command enters an audit log with the responsible gate. No measured performance or test outcome is supplied in the teamsheet.

## Slide 7
Path to industrial validation
CyberMACS Summer School 2026 Hackathon
07
01
PLC test rig
Modbus / OPC-UA integration
02
Hardware isolation
Physical key switch
03
Formal safety review
ISA-84 review and SIL-3 solver validation
04
Broader coverage
Chlorine and fluoride dosing
Notes: Next steps from the source: replace simulated sensors with Modbus/OPC-UA integration against a PLC test rig; implement a genuine air-gapped hardware key switch; pursue formal ISA-84 compliance review and validation against a certified SIL-3 logic solver; extend redundancy to chlorine and fluoride parameters. The current prototype is not claimed to be certified.

## Slide 8
CyberMACS Summer School 2026 Hackathon
08
THANK YOU
Project repository
github.com/devded/i1
AI tool disclosure
Claude Code assisted implementation.
The team owns the design
and safety-critical logic.